## README
SUPERWOOD × Data Centers — material mass, embodied carbon and replacement model (2026-09-04, v3)
Reference unit: 1 GW IT-load data center. Change any yellow cell on Inputs (and the four addressable-share columns on 1 GW data center — immediate, soon, medium term, long term; a row may split across them); everything recalculates.
Low column = every low input; High column = every high input. These are scenario bounds, not a distribution — vary single inputs for sensitivities.
Read the sheet 1 GW data center top to bottom: building structure and envelope first, then contents, with a running cumulative total. The right-hand columns show, for each component, the addressable share in each of the four horizons, the mass replaced, and the SUPERWOOD required (per-horizon SUPERWOOD split sits in grouped helper columns P–W). The summary block and chart follow.
Horizons: Immediate (shipping now, no assembly rating) · Soon (certification-gated non-structural: platforms, railings, barriers, racking, doors) · Medium term (structural steel, roof trusses and roofs, ducting, enclosures) · Long term (foundations). Switch Inputs walls_precast to 1 to model precast perimeter walls; foundation_share and conc_sub_factor drive the long-term row.
Provenance: concrete and structural-steel intensities are published, secondary (arXiv 2509.21312 citing Hasan 2022 / Sharma 2023, conf M); GB200 rack mass is NVIDIA-published (conf H). Everything else is estimated [conf: L] — replace with a real material takeoff from HITT, Turner or Fast + Epp before external use.
Embodied carbon: columns X–AB on the main sheet value each row at its own factor (concrete, steel, mixed; equipment not estimated), with totals and steel/concrete shares in the summary; the Carbon sheet rolls avoided emissions up by horizon at those factors and at the recycled-steel (EAF) factor. Steel share: the Steel share sheet estimates what fraction of above-ground mass, contents included, is steel (per-component steel fractions are yellow inputs).
Companion narrative: materials-mass-and-replacement.md in the same folder.

## Inputs
Parameter | Low | High | Unit | Label / confidence | Note
IT load of reference data center | 1000 | 1000 | MW | assumption | Everything downstream is linear in this
Building area per MW | 5000 | 10000 | sf/MW | estimated [L] | Hyperscale, single-story
Footprint per building | 1000000 | 1000000 | sf | estimated [L] | ~1,000 ft sides
Exterior wall area per building | 160000 | 160000 | sf | derived | 4 × 1,000 ft × 40 ft eave
Yard / mechanical screens and louvers (per data center) | 200000 | 500000 | sf | estimated [L]
Perimeter + yard fence length | 10 | 20 | km | estimated [L] | Data center perimeter plus transformer / generator yards
Fence height | 2.5 | 2.5 | m | assumption
Biophilic interior paneling (admin / office wings) | 100000 | 300000 | sf | estimated [L]
Backplanes, trim, door kicks, sub-framing | 50000 | 150000 | sf | estimated [L]
Concrete intensity (all concrete) | 500 | 1000 | m³/MW | published, secondary [M] | arXiv 2509.21312 citing Hasan 2022 / Sharma 2023: 5,000–10,000 m³ per 10 MW
Concrete density | 2.4 | 2.4 | t/m³ | published [H]
Walls are precast? (1 = yes, 0 = metal panel) | 0 | 0 | flag | choice | 1: facade mass moves from metal skins (immediate) to precast panels (long term)
Precast / tilt-up wall thickness | 0.2 | 0.2 | m | estimated [L] | 8 in
Structural steel intensity | 50 | 100 | t/MW | published, secondary [M] | Same source: 500–1,000 t per 10 MW
Share of structural steel that is secondary (trusses, joists, girts, deck) | 0.4 | 0.6 | share | estimated [L] | Remainder = primary frame
Rebar per m³ of concrete | 60 | 100 | kg/m³ | estimated [L]
Platforms, walkways, mezzanines, railings, tray supports | 5 | 15 | t/MW | estimated [L]
Metal panel / IMP cladding mass | 25 | 50 | kg/m² | estimated [L]
Louver / screen system mass | 10 | 20 | kg/m² | estimated [L]
Steel fence mass per running metre | 30 | 50 | kg/m | estimated [L] | Palisade / chain-link with posts
Acoustic barriers, enclosures, HVAC separations | 2 | 5 | t/MW | estimated [L]
Racking and equipment supports | 2 | 5 | t/MW | estimated [L]
Other tray, containment, doors, misc. metals | 5 | 10 | t/MW | estimated [L]
Interior finishes, backplanes, trim (mass) | 1 | 3 | t/MW | estimated [L] | Admin / office wings only
Electrical: gensets, transformers, switchgear, UPS, busway, copper | 50 | 100 | t/MW | estimated [L] | Genset 30–60 t, 1 MW UPS 10–20 t, transformer 5–8 t
Mechanical: chillers, fan walls, coolers, piping, water | 20 | 50 | t/MW | estimated [L]
Share of mechanical mass that is equipment shells, casings and fan-wall frames — SUPERWOOD in the medium term | 0.25 | 0.25 | share | estimated [L]; Alex 2026-09-06 | About half of the steel in the row; compressor and pump bodies, tubes and steel piping excluded
Share of mechanical mass that is fan blades — long term, needs investigation | 0.02 | 0.02 | share | estimated [L]; Alex 2026-09-06 | Aluminum or composite blades today; SUPERWOOD blades are a research question
IT: servers and racks | 15 | 70 | t/MW | estimated [L] | Loaded rack ~1 t; GB200 NVL72 ~1.36 t [H]
Share of IT mass that is server rack cabinets (frames, panels, doors) — substitutable soon | 0.18 | 0.18 | share | estimated [L]; Alex 2026-09-06 | A loaded rack of 1–1.4 t carries a 150–250 kg steel cabinet
Share of IT mass that is server enclosures (sheet-steel chassis) — long term | 0.3 | 0.3 | share | estimated [M]; analyses/it-rack-material-stack.md, applied 2026-09-06 | Server boxes eventually; the electronics never
Share of all concrete that is foundations, footings, piers and equipment pads | 0.4 | 0.5 | share | estimated [L] | Remainder is slab on grade, paving and yard
Long-term technical potential: share of slab-on-grade and paving concrete replaceable | 0.75 | 0.75 | share | asserted-internal (Alex, 2026-09-01) [L] | Technical potential, not a plan; no design or code pathway yet
Long-term technical potential: share of foundations, footings, piers and pads replaceable | 0.9 | 0.9 | share | asserted-internal (Alex, 2026-09-01) [L] | Technical potential, not a plan
kg SUPERWOOD per kg of concrete replaced | 0.05 | 0.15 | kg/kg | estimated [L] | Lightweight insulated wood-foundation concept; no design exists yet
Ducting, plenums and air-distribution sheet metal | 3 | 8 | t/MW | estimated [L] | Separate from the mechanical-equipment row
Concrete emissions | 0.12 | 0.12 | kg CO₂e/kg | industry range [M] | Ready-mix, cradle to gate; typical 0.10–0.15
Polymers in paints, foam cores and plastic trim (average) | 3 | 3 | kg CO₂e/kg | industry range [M]; Alex 2026-09-05 | Cradle to gate; polyolefins and PVC about 2–2.5, polyurethane foam 3–4, coatings higher
SUPERWOOD average board thickness | 7.2 | 7.2 | mm | internal TEM basis [H]
SUPERWOOD density | 1300 | 1300 | kg/m³ | internal TEM [H]
SuperMill One output | 1000000 | 1000000 | sf/yr | internal [H]
SuperMill Two output | 36000000 | 36000000 | sf/yr | internal [H]
Structural substitution: kg SUPERWOOD per kg steel replaced | 0.3 | 0.6 | kg/kg | estimated [L] | Engineering-stamped per element (Fast + Epp) before external use
SUPERWOOD in a hybrid wall panel replacing precast | 20 | 40 | kg/m² | estimated [L] | Panel design unsettled
Addressable share of other tray / containment / doors (medium term) | 0.5 | 0.5 | share | estimated [L]
Count rebar as addressable in the long term? (0/1) | 0 | 0 | flag | choice | Rebar is a frontier market with no pathway; off by default
Concrete basis: 0 = published per-MW intensity, 1 = footprint bottom-up (Foundations sheet) | 1 | 1 | switch | choice | Deck default since 2026-09-06 (Alex): footprint basis
Soil case for the footprint basis: 1 good (spread footings), 2 moderate (lean concrete, larger footings), 3 poor (piles, pile caps, structural slab) | 2 | 2 | switch | choice | Deck default since 2026-09-06 (Alex): moderate soils; the web deck has a soils slider
Hall slab on grade thickness | 6 | 8 | in | estimated [L]
Share of hall floor thickened (electrical rooms, dense rack rows) | 0.15 | 0.25 | share | estimated [L]
Thickened slab thickness | 10 | 12 | in | estimated [L]
Column bay | 40 | 40 | ft | estimated [L] | Square bays
Spread footing plan dimension | 8 | 10 | ft | estimated [L] | Square footings
Spread footing depth | 2 | 2.5 | ft | estimated [L]
Perimeter grade beam width | 2 | 2.5 | ft | estimated [L]
Perimeter grade beam depth | 3 | 3.5 | ft | estimated [L]
Generator unit size | 3 | 2.5 | MW | estimated [L] | Smaller units in the high case mean more pads
Generator redundancy factor | 1.1 | 1.25 | factor | estimated [L] | N+1 to N+25%
Generator pad volume | 480 | 787.5 | cf | estimated [L] | 40x12x1 ft to 45x14x1.25 ft
Transformer / switchgear pads per generator | 0.5 | 0.6 | count | estimated [L]
Transformer / switchgear pad volume | 300 | 562.5 | cf | estimated [L] | 20x15x1 ft to 25x18x1.25 ft
Mechanical equipment pads as a share of floor area | 0.05 | 0.08 | share | estimated [L] | Chillers, coolers, fan walls on grade or roof
Mechanical pad thickness | 8 | 10 | in | estimated [L]
Site paving, roads, yards, parking as a multiple of building footprint | 0.8 | 1.5 | ratio | estimated [L]
Site paving thickness | 6 | 8 | in | estimated [L]
Case 2: share of footprint over-excavated and replaced with lean concrete / CLSM | 0.3 | 0.6 | share | estimated [L]
Case 2: lean concrete thickness | 6 | 12 | in | estimated [L]
Case 2: enlargement of footings, grade beams and pads | 0.3 | 0.3 | factor | estimated [L]
Case 3: piles or drilled piers per column | 3 | 4 | count | estimated [L]
Case 3: pile diameter | 1.5 | 2 | ft | estimated [L]
Case 3: pile length | 40 | 60 | ft | estimated [L]
Case 3: pile cap volume per column (replaces the spread footing) | 300 | 504 | cf | estimated [L] | 10x10x3 ft to 12x12x3.5 ft
Case 3: pier spacing under grade beams | 20 | 15 | ft | estimated [L]
Case 3: slab thickening to a structural slab | 2 | 4 | in | estimated [L]
Substation / transformer yard mats per GW | 10 | 20 | acres | estimated [L]
Yard mat thickness | 18 | 24 | in | estimated [L]
Steel emissions, global average (BF-BOF) | 1.8 | 1.8 | kg CO₂e/kg | published-class [M]
Steel emissions, recycled (EAF) | 0.4 | 0.7 | kg CO₂e/kg | industry range [M]
SUPERWOOD manufacturing emissions | 0.5 | 0.5 | kg CO₂e/kg | internal, pre-LCA [L] | Canva DCII deck; LCA under way, Prof. Ming Hu, Notre Dame
SUPERWOOD biogenic carbon stored | 1.3 | 1.3 | kg CO₂e/kg | internal, pre-LCA [L] | Report separately; module C release under EN 15804
Interior finishes emissions (gypsum, wood, steel studs — mixed) | 1 | 1 | kg CO₂e/kg | estimated [L] | Used only for the interior finishes row

## 1 GW data center
Component (building, then contents) | Low tons per data center | High tons per data center | Low cumulative t | High cumulative t | Addressable — immediate | Addressable — soon | Addressable — medium term | Addressable — long term | Low replaced t | High replaced t | Low SUPERWOOD t | High SUPERWOOD t | Gate / basis | High not replaced t | Low SW immediate (helper — grouped, unhide to see the per-horizon split) | Low SW soon | Low SW medium | Low SW long | High SW immediate | High SW soon | High SW medium | High SW long | Carbon factor (kg CO₂e/kg) | Low embodied carbon (t CO₂e) | High embodied carbon (t CO₂e) | EAF-basis factor (kg CO₂e/kg) | Material class | Steel share | Concrete share | Plastic share | Other share
BUILDING — STRUCTURE AND ENVELOPE
Concrete: slab on grade, paving, yard |  |  |  |  | 0% | 0% | 0% | [5 empty] | Technical potential per Alex (75%); no design or code pathway yet. arXiv 2509.21312 [M] for total concrete | [13 empty] | concrete | 0 | 1 | 0 | 0
Concrete: foundations, footings, piers, equipment pads |  |  |  |  | 0% | 0% | 0% | [5 empty] | Technical potential per Alex (90%); lightweight insulated SUPERWOOD foundations — geotechnical, durability and code pathway all open | [13 empty] | concrete | 0 | 1 | 0 | 0
Precast / tilt-up perimeter walls (precast case) |  |  |  |  | 0% | 0% | 100% | 0% |  |  |  |  | Hybrid SUPERWOOD wall panels; NFPA 285 + E119 assemblies. Active when Inputs walls_precast = 1 | [13 empty] | concrete | 0 | 1 | 0 | 0
Rebar in all concrete |  |  |  |  | 0% | 0% | 0% | [5 empty] | Rebar follows the concrete it sits in: foundation share × 90% + slab share × 75% | [13 empty] | steel | 1 | 0 | 0 | 0
Structural steel — primary frame (columns, girders) |  |  |  |  | 0% | 0% | 100% | 0% |  |  |  |  | ICC-ES via the mass-timber qualification pathway; FM acceptance; E119 | [13 empty] | steel | 1 | 0 | 0 | 0
Structural steel — roof trusses, joists, roof deck, girts |  |  |  |  | 0% | 0% | 100% | 0% |  |  |  |  | Design values and connection data; trusses carry no fire-resistance requirement | [13 empty] | steel | 1 | 0 | 0 | 0
Exterior skins — metal panel / IMP (metal-panel case) |  |  |  |  | 100% | 0% | 0% | 0% |  |  |  |  | Shipping now; area-for-area rain screen | [13 empty] | steel | 0.65 | 0 | 0.3 | 0.05
Louvers and yard / mechanical screens |  |  |  |  | 100% | 0% | 0% | 0% |  |  |  |  | Shipping now | [13 empty] | steel | 1 | 0 | 0 | 0
Security and staff-area fencing |  |  |  |  | 100% | 0% | 0% | 0% |  |  |  |  | Shipping now — the Microsoft near-term list | [13 empty] | steel | 1 | 0 | 0 | 0
CONTENTS — FIT-OUT AND EQUIPMENT
Platforms, walkways, mezzanines, railings, tray supports |  |  |  |  | 0% | 100% | 0% | 0% |  |  |  |  | Published design values; IBC 1607 for railings | [13 empty] | steel | 1 | 0 | 0 | 0
Acoustic barriers, enclosures, HVAC separations |  |  |  |  | 0% | 100% | 0% | 0% |  |  |  |  | STC / OITC lab and field data | [13 empty] | steel | 0.7 | 0 | 0.05 | 0.25
Racking and equipment supports |  |  |  |  | 0% | 100% | 0% | 0% |  |  |  |  | A few months of design and load-data development (Alex 2026-09-04) | [13 empty] | steel | 1 | 0 | 0 | 0
Other tray, containment, doors, misc. metals |  |  |  |  | 0% |  | 0% | 0% |  |  |  |  | Partial; UL 10C for rated doors | [13 empty] | steel | 1 | 0 | 0 | 0
Ducting, plenums and air-distribution sheet metal |  |  |  |  | 0% | 0% | 100% | 0% |  |  |  |  | NFPA 90A / UL 181 noncombustibility expectations for in-airstream components — the hardest gate in this row set | [13 empty] | steel | 1 | 0 | 0 | 0
Interior finishes, backplanes, trim (admin / office) |  |  |  |  | 100% | 0% | 0% | 0% |  |  |  |  | E84 Class A finish; backplanes UL 94 yellow card (not yet started) | [13 empty] | mixed | 0.3 | 0 | 0.1 | 0.6
Electrical equipment and conductors |  |  |  |  | 0% | 0% | 0% | 0% |  |  |  |  | Gensets, transformers, switchgear, batteries, copper | [13 empty] | equipment | 0.6 | 0 | 0.05 | 0.35
Mechanical equipment, piping, loop water |  |  |  |  | 0% | 0% | [6 empty] | Shells, casings and fan-wall frames medium term (Alex 2026-09-06); fan blades long term, needs investigation; compressors, pumps, tubes, piping and water stay | [13 empty] | equipment | 0.5 | 0 | 0.05 | 0.45
IT — servers and racks |  |  |  |  | 0% |  | 0% | [5 empty] | Rack cabinets soon (18% of IT mass), server enclosures long term (30%), per analyses/it-rack-material-stack.md; electronics never. Rack masses [H]; aggregate [L] | [13 empty] | equipment | 0.5 | 0 | 0.08 | 0.42
SUMMARY — per data center
Total mass, building and contents (tons)
Total excluding concrete (tons)
Replaced by SUPERWOOD, by horizon
Immediate — incumbent mass replaced (tons)
Immediate — SUPERWOOD required (tons)
Immediate — SUPERWOOD required (sf)
Immediate — years of SuperMill One output
Soon — incumbent mass replaced (tons)
Soon — SUPERWOOD required (tons)
Soon — years of SuperMill Two output
Medium term — incumbent mass replaced (tons)
Medium term — SUPERWOOD required (tons)
Medium term — years of SuperMill Two output
Long term — incumbent mass replaced (tons)
Long term — SUPERWOOD required (tons)
Long term — years of SuperMill Two output
Cumulative incumbent mass replaced (tons)
Cumulative SUPERWOOD required (tons)
Cumulative years of SuperMill Two output
Share of total mass replaced
Share of ex-concrete mass replaced through the medium term (excludes foundations)
Not replaced by SUPERWOOD (tons)
Not replaced, share of total
EMBODIED CARBON — building materials (equipment not estimated)
Embodied carbon, building materials (t CO₂e)
of which steel (t CO₂e)
of which concrete (t CO₂e)
Steel share of building-materials carbon
Concrete share of building-materials carbon
Steel above the slab (steel excl. rebar), share of building-materials carbon
Steel share if steel is recycled (EAF factor, high end)

## Derived
Quantity | Low | High | Unit
Number of buildings |  |  | count
Exterior wall area, sf |  |  | sf
Exterior wall area, m² |  |  | m²
Fence face area, sf |  |  | sf
SUPERWOOD board mass per sf |  |  | kg/sf
SuperMill One output in tonnes |  |  | t/yr
SuperMill Two output in tonnes |  |  | t/yr

## Foundations
Element | Low m³ | High m³ | Basis
Building floor area, sf |  |  | from Inputs
Total hall perimeter, ft |  |  | buildings x 4 sides
Columns |  |  | one per bay
Hall slab on grade |  |  | 6–8 in over the floor
Thickened slab zones |  |  | extra depth over 15–25% of the floor
Column footings |  |  | spread footings, good soils
Perimeter grade beams
Generators |  |  | units incl. redundancy
Generator pads
Transformer and switchgear pads
Mechanical equipment pads
Case 1 good soils — building and pads |  |  | sum
Case 2 — lean concrete / CLSM under footprint
Case 2 — larger footings, grade beams and pads
Case 2 moderate soils — allowance |  |  | added to case 1
Case 3 — piles or drilled piers under columns
Case 3 — pile caps net of spread footings
Case 3 — piers under grade beams
Case 3 — structural slab thickening
Case 3 poor soils — allowance (includes the case 2 measures) |  |  | nested: ground replacement and larger elements plus piles, caps, piers and a structural slab
Selected soil allowance |  |  | Inputs soil_case
Site paving, roads, yards, parking
Substation / transformer yard mats
All-in with site work, selected soil case |  |  | sum
Slab and paving, footprint basis (m³) |  |  | feeds the main sheet when concrete_basis = 1
Foundations, footings and pads, footprint basis (m³) |  |  | feeds the main sheet when concrete_basis = 1; soil cases nest
Slab and paving, footprint basis (t)
Foundations, footings and pads, footprint basis (t)
Per-MW basis for comparison (m³) |  |  | published, secondary
Wall system: tilt-up versus insulated metal panel is the Inputs walls_precast switch (precast row on the main sheet, steel-share sheet reports both). Soil cases and the concrete basis switch are Inputs soil_case and concrete_basis. All element inputs are estimates [L]; see foundation-bottom-up.md.

## Carbon
Horizon | Low incumbent emissions avoided (t CO₂e) | High | Low SUPERWOOD manufacturing (t CO₂e) | High | Low net reduction | High | Low net vs EAF steel | High | Low biogenic stored (separate) | High
Immediate (steel)
Soon (steel)
Medium term (steel)
Long term (concrete, rebar, server enclosures)
Pre-LCA projections (LCA under way with Prof. Ming Hu, University of Notre Dame). Each row is valued at its own factor (column X on the main sheet): concrete rows at co2_conc, steel rows including rebar at co2_steel, interior finishes at co2_mixed; equipment rows (including the long-term server enclosures) carry no factor, so the long-term row counts concrete and rebar only. The EAF column revalues steel rows at the recycled-steel factor (high end). Equipment rows carry no factor. Biogenic storage reported separately (EN 15804 module C).

## Steel share
Above-ground component (contents included) | Low tons | High tons | Steel fraction — low | Steel fraction — high | Low steel tons | High steel tons | Basis for the fraction
Precast / tilt-up perimeter walls (precast case) |  |  | 3% | 5% |  |  | rebar in precast/tilt-up panels; row is zero unless Inputs walls_precast = 1
Structural steel — primary frame (columns, girders) |  |  | 100% | 100% |  |  | steel by definition
Structural steel — roof trusses, joists, roof deck, girts |  |  | 100% | 100% |  |  | steel by definition
Exterior skins — metal panel / IMP (metal-panel case) |  |  | 85% | 95% |  |  | steel-faced IMP; some aluminum
Louvers and yard / mechanical screens |  |  | 40% | 70% |  |  | aluminum common
Security and staff-area fencing |  |  | 90% | 100% |  |  | chain-link, palisade, posts
Platforms, walkways, mezzanines, railings, tray supports |  |  | 95% | 100% |  |  | structural and misc. steel
Acoustic barriers, enclosures, HVAC separations |  |  | 70% | 90% |  |  | steel panels with absorptive fill
Racking and equipment supports |  |  | 95% | 100% |  |  | steel
Other tray, containment, doors, misc. metals |  |  | 85% | 95% |  |  | mostly steel, some aluminum
Ducting, plenums and air-distribution sheet metal |  |  | 95% | 100% |  |  | galvanized steel
Interior finishes, backplanes, trim (admin / office) |  |  | 20% | 40% |  |  | gypsum, wood, steel studs
Electrical equipment and conductors |  |  | 50% | 65% |  |  | enclosures, cores, gensets, switchgear; rest copper, oil, batteries
Mechanical equipment, piping, loop water |  |  | 45% | 65% |  |  | chillers, piping steel; water, copper, refrigerant not
IT — servers and racks |  |  | 40% | 60% |  |  | steel chassis and racks; aluminum, PCBs, copper
Above-ground mass, contents included (tons)
Steel in it (tons)
Steel share of above-ground mass
Steel share including slab rebar (at-grade steel)
Structure and envelope only (first five rows)
WALL SYSTEM CASES (independent of the Inputs toggle)
Tilt-up / precast wall mass if chosen (tons)
Metal-panel skin mass if chosen (tons)
Steel share — metal-panel walls
Steel share — tilt-up / precast concrete walls
Excludes slab on grade, paving and foundations. The wall system matters: the main block follows Inputs walls_precast (0 = metal panel, 1 = tilt-up/precast); the two case rows above force each wall system regardless of the toggle. Steel fractions per component are estimates [conf: L] (yellow cells). Printed band on the deck: 50–80% (Alex, 2026-09-04), covering both wall systems.